## Revision
V0 | 2017-02-23 | Création du document
V1 | 2017-10-23 | Saved the first tracked version
V2 | 2017-11-15 | Modifications on the "General" sheet
V3 | 2017-11-27 | Modifications on the "General" sheet
V4 | 2017-12-05
V5 | 2017-12-13 | Modifications at CryoDiffusion
V6 | 2018-03-01 | Update in "General" and "Sequences" sheets
V7 | 2018-06-05
V8 | 2020-10-14 | Added new parameter to SQ22 & SQ23
V9 | 2020-12-02 | Added new parameter for SQ18. Added new status bit in general status. Removed unused data related to CV5203.
V10 | 2021-04-01 | Added support for Changing the PID parameters from Epics

## Equipments
EPICS Dialog
Digital Input | [7 empty] | All the time :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Copy of input is the physical input
Type "Epi_to_Plc_DI" |  |  |  | Type "Plc_to_Epi_DI" |  |  |  | Normal mode :
DBX0.0 | Bool | cmdNorm | Set Normal | DBX0.0 | Bool | sForced | Copy of Normal/Forced mode (0=Normal / 1=Forced) |  | Copy of Calculate Input is the delay input
DBX0.1 | Bool | cmdForced | Set Forced | DBX0.1 | Bool | sInp | Copy of Input | Forced mode :
DBX0.2 | Bool | cmdSet | Set forced command | DBX0.2 | Bool | sProcInp | Copy of Calculate Input |  | Copy of Calculate Input is the Forced command
DBX0.3 | Bool | cmdRst | Reset forced command | DBX0.3 | Bool
DBX0.4 | Bool |  |  | DBX0.4 | Bool
DBX0.5 | Bool |  |  | DBX0.5 | Bool
DBX0.6 | Bool |  |  | DBX0.6 | Bool
DBX0.7 | Bool |  |  | DBX0.7 | Bool
Process Analog Input
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | sRdV is always the phisical input
Type "Epi_to_Plc_AI" |  |  |  | Type "Plc_to_Epi_AI"
DBX0.0 | Bool | cmdNorm | Set Normal | DBX0.0 | Bool | sForced | Copy of Normal/Forced mode (0=Normal / 1=Forced) |  | sSetV is always a copy of Manual value
DBX0.1 | Bool | cmdForced | Set Forced | DBX0.1 | Bool
DBX0.2 | Bool | cmdSet | Set forced command | DBX0.2 | Bool
DBD2 | Real | cSetV | Manual Value | DBD2 | Real | sRdV | Process Value
|  |  |  | DBD6 | Real | sRealRdV | Real Process Values (as read from the input)
Valves | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Command is controled by program
Type "Epi_to_Plc_Valve" |  |  |  | Type "Plc_to_Epi_Valve" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Command is controled by manual command
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool | sSim | Copy of Simulation mode (1=Simulation)
DBX0.2 | Bool | cmdSet | Set manual command | DBX0.2 | Bool | sCmd | Copy of Command | Inhibition mode :
DBX0.3 | Bool | cmdRst | Reset manual command | DBX0.3 | Bool | sOn | Copy of On sensor(in Normal mode) - Simulated (in Simulation mode) |  | Faults are disable and sensor are simulated
DBX0.4 | Bool | cmdAck | Set Acknoledge | DBX0.4 | Bool | sOff | Copy of Off sensor(in Normal mode) - Simulated (in Simulation mode)
DBX0.5 | Bool | cmdSimSet | Set Simulation mode | DBX0.5 | Bool | sNO | Type of valve (0=Normally Closed - 1=Normally Open)
DBX0.6 | Bool | cmdSimRst | Reset Simulation mode | DBX0.6 | Bool | sOnFlt | Copy of fault On
DBX0.7 | Bool |  |  | DBX0.7 | Bool | sOffFlt | Copy of fault Off
|  |  |  | DBX1.0 | Bool | sFlt | LogicalsSum of sOnFlt and sOffFlt
|  |  |  | DBX1.1 | Bool | sCmdAuto | Copy of command in Auto mode
Electrovalves | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Command is controled by program
Type "Epi_to_Plc_EV" |  |  |  | Type "Plc_to_Epi_EV" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Command is controled by manual command
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool | sCmd | Copy of Command
DBX0.2 | Bool | cmdSet | Set manual command | DBX0.2 | Bool | sCmdAuto | Copy of command in Auto mode
DBX0.3 | Bool | cmdRst | Reset manual command | DBX0.3 | Bool
DBX0.4 | Bool |  |  | DBX0.4 | Bool
DBX0.5 | Bool |  |  | DBX0.5 | Bool
DBX0.6 | Bool |  |  | DBX0.6 | Bool
DBX0.7 | Bool |  |  | DBX0.7 | Bool
Analog Valves | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Output value is controled by program
Type "Epi_to_Plc_AnaValve" |  |  |  | Type "Plc_to_Epi_AnaValve" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Output value is controled by manual value
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool
DBX0.2 | Bool | cmdSet | Set manual command | DBX0.2 | Bool
DBD2 | Real | cSetV | Manual Value | DBD2 | Real | sRdV | Output Value
|  |  |  | DBD6 | Real | sAutoRdV | Automatic value
PID | [7 empty] | Auto mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Output mode is set to Automatic
Type "Epi_to_Plc_PID" |  |  |  | Type "Plc_to_Epi_PID" |  |  |  |  | Output value is controled by regulator with automatic Setpoint
DBX0.0 | Bool | cmdAuto | Set Auto (controlled by PLC) | DBX0.0 | Bool | sAuto | Copy of Auto/manual mode (1=Auto / 0=Manual) | Manual mode :
DBX0.1 | Bool | cmdMan | Set Norm (controlled by the operator) SPV ) | DBX0.1 | Bool | sRegOn | Copy of RegulatorOn/RegulatorOff mode (1=RegulatorOn / 0=RegulatorOff) |  | Operator can change Output mode
DBX0.2 | Bool | cmdRegOn | Set Output from setpoint via PID regulator | DBX0.2 | Bool |  |  |  | Output mode in RegulatorOn :
DBX0.3 | Bool | cmdRegOff | Set Output from local Output | DBX0.3 | Bool |  |  |  |  | Output value is controled by regulator with Local Setpoint
DBX0.4 | Bool | cmdSetP | Set Local Setpoint | [5 empty] | Output mode in RegulatorOff :
DBX0.5 | Bool | cmdOutput | Set Local Output | DBD2 | Real | sSetP | Actual setpoint |  |  | Output value is controled by Local Output
|  |  |  | DBD6 | Real | sOutV | Actual Output
DBD2 | Real | cSetP | Local Setpoint | DBD10 | Real | sKp | Gain
DBD6 | Real | cOutput | Local Output | DBD14 | Real | sTi | Integral time
|  |  |  | DBD18 | Real | sTd | Derived time
PID_Param | [8 empty] | Added in V10
EPICS -> PLC |  |  |  | PLC -> EPICS
Type "Epi_to_Plc_PID_Param" |  |  |  | None
DBX0.0 | Bool | cmdAuto | Not used
DBX0.1 | Bool | cmdMan | Not used
DBX0.2 | Bool | cmdRegOn | Not used
DBX0.3 | Bool | cmdRegOff | Not used
DBX0.4 | Bool | cmdSetP | Not used
DBX0.5 | Bool | cmdOutput | Not used
DBX0.6 | Bool | cmdOutput | Not used
DBX0.7 | Bool | cmdOutput | Not used
DBX1.0 | Bool | cmdOutput | Not used
DBX1.1 | Bool | cmdOutput | Not used
DBX1.2 | Bool | cmdOutput | Not used
DBX1.3 | Bool | cmdKp | Set gain
DBX1.4 | Bool | cmdTi | Set integration time
DBX1.5 | Bool | cmdTd | Set differentaition tim
DBD2 | Real | cKp | Gain
DBD6 | Real | cTi | Ti
DBD10 | Real | cTd | Td
Heater (type 1) | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Command is controled by program
Type "Epi_to_Plc_Heater" |  |  |  | Type "Plc_to_Epi_Heater" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Command is controled by manual command
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool | sTsw | Copy of Thermoswitch
DBX0.2 | Bool | cmdSet | Set manual command | DBX0.2 | Bool | sCmd | Copy of command | All times :
DBX0.3 | Bool | cmdRst | Reset manual command | DBX0.3 | Bool | sCmdAuto | Copy of command in Auto mode |  | If Thermoswitch is ON then command is disable.
DBX0.4 | Bool | cmdHL | Set High limit | DBX0.4 | Bool | sHtrOn | State of the heater (in versions <123 sCmd behaved as this bit now)
DBX0.5 | Bool | cmdLL | Set Low Limit | DBX0.5 | Bool
DBX0.6 | Bool |  |  | DBX0.6 | Bool
DBX0.7 | Bool |  |  | DBX0.7 | Bool
DBD2 | Real | cHL | High limit | DBD2 | Real | sHL | State High limit
DBD6 | Real | cLL | Low Limit | DBD6 | Real | sLL | State Low Limit
Heater (type 2) | [7 empty] | Automatic mode :
EPICS -> PLC |  |  |  | PLC -> EPICS |  |  |  |  | Commands (1, 2 & 3) are controled by program
Type "Epi_to_Plc_Heater2" |  |  |  | Type "Plc_to_Epi_Heater2" |  |  |  | Manual mode :
DBX0.0 | Bool | cmdAuto | Set Auto | DBX0.0 | Bool | sAuto | Copy of Auto/Manual mode (1=Auto / 0=Manual) |  | Commands (1, 2 & 3) are controled by manuals commands (1, 2 & 3)
DBX0.1 | Bool | cmdMan | Set Manual | DBX0.1 | Bool | sTsw | Copy of Thermoswitch
DBX0.2 | Bool | cmdSet1 | Set manual command 1 | DBX0.2 | Bool | sCmd1 | Copy of command 1 | All times :
DBX0.3 | Bool | cmdRst1 | Reset manual command 1 | DBX0.3 | Bool | sCmd2 | Copy of command 2 |  | If Thermoswitch is ON then commands are disable.
DBX0.4 | Bool | cmdSet2 | Set manual command 2 | DBX0.4 | Bool | sCmd3 | Copy of command 3
DBX0.5 | Bool | cmdRst2 | Reset manual command 2 | DBX0.5 | Bool | sLs | Copy of Water Level switch
DBX0.6 | Bool | cmdSet3 | Set manual command 3 | DBX0.6 | Bool | sHtrOn | Copy of Input Heater On
DBX0.7 | Bool | cmdRst3 | Reset manual command 3 | DBX0.7 | Bool | sSim | Copy of Simulation mode (1=Simulation)
DBX1.0 | Bool | cmdAck | Set Acknoledge | DBX1.0 | Bool | sFlt | Copy of fault
DBX1.1 | Bool | cmdSimSet | Set Simulation mode
DBX1.2 | Bool | cmdSimRst | Reset Simulation mode
DBX1.3 | Bool | cmdL1 | Set limit 1
DBX1.4 | Bool | cmdL2 | Set limit 2
DBX1.5 | Bool | cmdL3 | Set limit 3
DBX1.6 | Bool
DBX1.7 | Bool
DBD2 | Real | cL1 | limit 1 | DBD2 | Real | sL1 | limit 1
DBD6 | Real | cL2 | limit 2 | DBD6 | Real | sL2 | limit 2
DBD10 | Real | cL3 | limit 3 | DBD10 | Real | sL3 | limit 3

## Sequences
Sequences |  |  |  | SQ0 |  | SQ1 |  | SQ2 |  | SQ3 |  | SQ4 |  | SQ5 |  | SQ6 |  | SQ7 |  | SQ8 |  | SQ9 |  | SQ10 |  | SQ11 |  | SQ12 |  | SQ13 |  | SQ13A |  | SQ14 |  | SQ15 |  | SQ16 |  | SQ17 |  | SQ18 |  | SQ19 |  | SQ20 |  | SQ21 |  | SQ22 |  | SQ23 |  | SQ24 |  | SQ25
EPICS -> PLC |  |  |  | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment
Type "Epi_to_Plc_Seq"
DBX0.0 | Bool | cmdStart | Start - Command
DBX0.1 | Bool | cmdStop | Stop - Command
DBX0.2 | Bool | cmdPause | pause - Command | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable
DBX0.3 | Bool | cmdResume | Resume - Command | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable |  | Never applicable
DBX0.4 | Bool | cmdReset | Reset - Command
DBX0.5 | Bool | cmdAccept | Acceptation - Command |  |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid |  | Valid
DBX0.6 | Bool | cmdSetParam | Write parameters - Commands
DBX0.7 | Bool | cmdMsg_Yes | Message - Yes answer |  |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  |  |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes |  | Msg_Yes
DBX1.0 | Bool | cmdMsg_No | Message - No answer |  |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  |  |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No |  | Msg_No
DBX1.1 | Bool | cmdSpare1 | Command - Spare | [18 empty] | Stop_Liquefier | SPV-API Stop command for liquefier mode | [18 empty] | sQuench_Ignore | Status of the quench ignore flag
DBX1.2 | Bool | cmdSpare2 | Command - Spare | [18 empty] | Stop_Dewar | SPV-API Stop command for dewar mode
DBX2.0 | Bool | cParB1 | Bool - Sequence parameter | [40 empty] | P_IL650 | Parameter : Selection IL | [8 empty] | P_Cry_iso | Parameter : Cryostat isolated=1 or not=0 | P_Cry_iso | Parameter : Cryostat isolated=1 or not=0
DBX2.1 | Bool | cParB2 | Bool - Sequence parameter | [40 empty] | P_IL651 | Parameter : Selection IL
DBX2.2 | Bool | cParB3 | Bool - Sequence parameter | [40 empty] | P_IL652 | Parameter : Selection IL
DBX2.3 | Bool | cParB4 | Bool - Sequence parameter | [40 empty] | P_IL653 | Parameter : Selection IL
DBX2.4 | Bool | cParB5 | Bool - Sequence parameter
DBX2.5 | Bool | cParB6 | Bool - Sequence parameter
DBX2.6 | Bool | cParB7 | Bool - Sequence parameter
DBX2.7 | Bool | cParB8 | Bool - Sequence parameter
DBW4 | Int | cParI1 | Integer - Sequence parameter |  |  | P_Nb_Cycle | Parameter : Setpoint Number of cycle | P_Nb_Cycle | Parameter : Setpoint Number of cycle | P_Nb_Cycle | Parameter : Setpoint Number of cycle | [10 empty] | P_Liq_Dew | Parameter - He supply mode (1=Liquefier 2=Dewar) | P_Reg_Int | Parameter : Mode (1=Intermittent 2=Regulation ) | P_T_Open_Cir | Parameter - Time for opening circuit | P_Reg_Int | Parameter : Mode (1=Intermittent 2=Regulation) | P_Reg_Int | Parameter : Mode (1=Intermittent 2=Regulation )
DBW6 | Int | cParI2 | Integer - Sequence parameter |  |  | P_Tempo_Starting | Parameter : Time of starting | P_Tempo_Starting | Parameter : Time of starting | P_Tempo_Starting | Parameter : Time of starting | [10 empty] | P_Reg_Int | Parameter - Mode (1=Intermittent 2=Regulation) |  |  | P_T_Start_Compress | Parameter - Time for starting compressor
DBW8 | Int | cParI3 | Integer - Sequence parameter |  |  | P_Te_Vac_Al | Parameter : Time of vacuum alarm | P_Te_Vac_Al | Parameter : Time of vacuum alarm | P_Te_Vac_Al | Parameter : Time of vacuum alarm | [14 empty] | P_Mode_Regul | Parameter - Regulation mode (1=InletTemp 2=OutletTemp 3=Flow)
DBW10 | Int | cParI4 | Integer - Sequence parameter |  |  | P_Te_HL_Vac_Al | Parameter : Time of high level vacuum alarm | P_Te_HL_Vac_Al | Parameter : Time of high level vacuum alarm | P_Te_HL_Vac_Al | Parameter : Time of high level vacuum alarm | [32 empty] | P_Sel_SP_CV650 | Parameter : Selection Setpoint (1=Flow 2=Temperature)
DBW12 | Int | cParI5 | Integer - Sequence parameter |  |  | P_Te_Pressure_Al | Parameter : Time of pressure alarm | P_Te_Pressure_Al | Parameter : Time of pressure alarm | P_Te_Pressure_Al | Parameter : Time of pressure alarm | [32 empty] | P_Sel_SP_CV651 | Parameter : Selection Setpoint (1=Flow 2=Temperature)
DBW14 | Int | cParI6 | Integer - Sequence parameter |  |  | P_Te_LL_Pre_Al | Parameter : Time of low level pressure alarm | P_Te_LL_Pre_Al | Parameter : Time of low level pressure alarm | P_Te_LL_Pre_Al | Parameter : Time of low level pressure alarm | [32 empty] | P_Sel_SP_CV652 | Parameter : Selection Setpoint (1=Flow 2=Temperature)
DBW16 | Int | cParI7 | Integer - Sequence parameter | [40 empty] | P_Sel_SP_CV653 | Parameter : Selection Setpoint (1=Flow 2=Temperature)
DBW18 | Int | cParI8 | Integer - Sequence parameter
DBW20 | Int | ReservedI9 | Integer - Sequence parameter |  |  | Not to be used by any sequence
DBD22 | Real | cParR1 | Real - Sequence parameter |  |  | P_Vacuum | Parameter : Pressure Vacuum | P_Vacuum | Parameter : Pressure Vacuum | P_Vacuum | Parameter : Pressure Vacuum |  |  | P_Cool_Down_Tt | Parameter : Cool down temperature | P_Cool_Down_Tt | Parameter : Cool down temperature | P_Cool_Down_Tt | Parameter : Cool down temperature | P_Sec_Tt_Low_LT600 | Parameter - Low Temperature Security for Level | P_CV600 | Parameter : Order for Analog Valves | P_LI670_max | Parameter - Maximum level | P_SP_CV380_TT371 | Parameter - Setpoint TT371 for CV380 | P_CV602 | Parameter - Order for Analog Valves | P_CV603 | Parameter : Order for Analog Valves |  |  | P_CV601 | Parameter : Order for Analog Valves | P_LI680_max | Parameter - Maximum level | P_SP_CV602_LT | Parameter - Setpoint LT682 for CV602 | P_LT683_min | Parameter - Minimum level | P_LI680_max | Parameter - Maximum level | P_SP_CV650_TT | Parameter - Setpoint TT654 for CV650 | P_SP_TT645 | Parameter - Setpoint Temperature | P_CV580 | Parameter - Order for Analog Valves | P_CV581 | Parameter - Order for Analog Valves | P_CV581 | Parameter - Order for Analog Valves | P_CV581 | Parameter - Order for Analog Valves | P_CV580 | Parameter - Order for Analog Valves
DBD26 | Real | cParR2 | Real - Sequence parameter |  |  | P_Vacuum_Max | Parameter : Pressure Vacuum max | P_Vacuum_Max | Parameter : Pressure Vacuum max | P_Vacuum_Max | Parameter : Pressure Vacuum max |  |  | P_TT705_low | Parameter : Low temperature cooling EV700 | P_TT745_low | Parameter : Low temperature cooling EV740 | P_TT766_low | Parameter : Low temperature cooling EV700 | P_Sec_Tt_Hig_LT600 | Parameter - High Temperature Security for Level | P_CV580 | Parameter : Order for Analog Valves | P_LI670_min | Parameter - Minimum level | P_SP_CV380_TT372 | Parameter - Setpoint TT372 for CV380 |  |  | P_CV581 | Parameter : Order for Analog Valves |  |  | P_LI660_max | Parameter - Maximum level | P_PT660_max | Parameter - Maximum pressure | P_SP_CV583_PT | Parameter - Setpoint PT681 for CV583 | P_SP_CV582_PT | Parameter - Setpoint PT660 for CV582 | P_LT682_min | Parameter - Minimum level | P_SP_CV650_FT | Parameter - Setpoint FT650 for CV650 | P_SP_LI670 | Parameter - Setpoint Level | P_LT600min | Parameter - Low level | P_CV583 | Parameter - Order for Analog Valves | P_CV583 | Parameter - Order for Analog Valves | P_CV583 | Parameter - Order for Analog Valves | P_Pressure_max | Parameter - Max pressure for alarm
DBD30 | Real | cParR3 | Real - Sequence parameter |  |  | P_He | Parameter : Pressure He | P_He | Parameter : Pressure He | P_He | Parameter : Pressure He |  |  | P_TT705_high | Parameter : High temperature cooling EV700 | P_TT745_high | Parameter : High temperature cooling EV740 | P_TT766_high | Parameter : High temperature cooling EV760 | P_Sec_Tt_Low_LI660 | Parameter - Low Temperature Security for Level | P_CV_He_Liq | Parameter : Order for Analog Valves | P_SP_CV602_LT | Parameter - Setpoint LI670 for CV602 | P_SP_CV380_FT | Parameter - Setpoint FT380 for CV380 | P_SP_CV602_FT | Parameter - Setpoint FT581 for CV602 | P_CV582 | Parameter : Order for Analog Valves |  |  | P_LI670_max | Parameter - Maximum level | P_PT681_max | Parameter - Maximum pressure | P_SP_CV680_LT | Parameter - Setpoint LT683 for CV680 | P_CV581 | Parameter - Order for Analog Valves | P_SP_CV602_LT | Parameter - Setpoint LT682 for CV602 | P_SP_CV651_TT | Parameter - Setpoint TT655 for CV651 | P_SP_CV590_PT | Parameter - Setpoint PT590 for CV590 |  |  | P_CV740 | Parameter - Order for Analog Valves | P_LI660min | Parameter - Low level | P_Pressure_max | Parameter - Max pressure for alarm
DBD34 | Real | cParR4 | Real - Sequence parameter |  |  | P_He_Min | Parameter : Pressure He min | P_He_Min | Parameter : Pressure He min | P_He_Min | Parameter : Pressure He min |  |  | P_CV700 | Parameter : Order valve | P_TT747_low | Parameter : Low temperature cooling EV744 | P_TT767_low | Parameter : Low temperature cooling EV762 | P_Sec_Tt_Hig_LI660 | Parameter - High Temperature Security for Level | P_CV590 | Parameter : Order for Analog Valves | P_LI660_max | Parameter - Maximum level | P_CV380 | Parameter - Order for Analog Valves | P_SP_CV581_PT | Parameter - Setpoint PT660 for CV581 | P_SP_CV582_PT660 | Parameter - Setpoint PT660 for CV582 |  |  | P_TT665_max | Parameter - Maximum Temperature | P_CV601 | Parameter : Order for Analog Valves | P_SP_CV581_PT | Parameter - Setpoint PT660 for CV581 | P_CV582 | Parameter - Order for Analog Valves | P_SP_CV583_PT | Parameter - Setpoint PT681 for CV583 | P_SP_CV651_FT | Parameter - Setpoint FT651 for CV651 | P_SP_LT590 | Parameter - Setpoint Level |  |  | P_LI670min | Parameter - Low level | P_LI670min | Parameter - Low level
DBD38 | Real | cParR5 | Real - Sequence parameter |  |  | P_CV600 | Parameter : Order for Analog Valves | P_CV581 | Parameter : Order for Analog Valves | P_CV380 | Parameter : Order for Analog Valves |  |  | P_TT700_warm | Parameter : Temperature warm EV700 | P_TT747_high | Parameter : High temperature cooling EV744 | P_TT767_high | Parameter : High temperature cooling EV762 | P_Sec_Tt_Low_LI670 | Parameter - Low Temperature Security for Level | P_LT600_min | Parameter - Minimum level | P_LI660_min | Parameter - Minimum level |  |  | P_SP_CV602_LI660 | Parameter - Setpoint LI660 for CV602 | P_SP_CV603_FT | Parameter - Setpoint FT551 for CV603 |  |  | P_TT665_min | Parameter - Minimum Temperature | P_CV602 | Parameter : Order for Analog Valves |  |  | P_PT660 | Parameter - Pressure control | P_SP_CV680_LT | Parameter - Setpoint LT683 for CV680 | P_SP_CV652_TT | Parameter - Setpoint TT656 for CV652 | P_SP_LI680 | Parameter - Setpoint Level |  |  | P_LI680min | Parameter - Low level | P_LI680min | Parameter - Low level
DBD42 | Real | cParR6 | Real - Sequence parameter |  |  | P_CV601 | Parameter : Order for Analog Valves | P_CV582 | Parameter : Order for Analog Valves |  |  |  |  | P_TT700_cold | Parameter : Temperature cold EV700 | P_TT750_low | Parameter : Low temperature cooling EV748 | P_TT760_warm | Parameter : Temperature warm EV760 | P_Sec_Tt_Hig_LI670 | Parameter - High Temperature Security for Level | P_LT600_max | Parameter - Maximum level | P_SP_CV602_LI660 | Parameter - Setpoint LI660 for CV602 |  |  | P_SP_CV602_LI670 | Parameter - Setpoint LI670 for CV602 | P_SP_CV603_LI660 | Parameter - Setpoint LI660 for CV603 |  |  | P_SP_CV581_PT | Parameter - Setpoint PT660 for CV581 | P_CV581 | Parameter : Order for Analog Valves |  |  | P_PT548 | Parameter - Pump at atmospheric pressure | P_CV583 | Parameter - Order for Analog Valves | P_SP_CV652_FT | Parameter - Setpoint FT652 for CV652 | P_CV590 | Parameter - Order for Analog Valves |  |  | P_FT581max | Parameter - max flow | P_FT581max | Parameter - max flow
DBD46 | Real | cParR7 | Real - Sequence parameter |  |  | P_CV602 | Parameter : Order for Analog Valves | P_CV583 | Parameter : Order for Analog Valves | [6 empty] | P_TT750_high | Parameter : High temperature cooling EV748 | P_TT760_cold | Parameter : Temperature cold EV760 | P_Sec_Tt_Low_LI680 | Parameter - Low Temperature Security for Level | P_SP_CV600_LT | Parameter - Setpoint LT600 for CV600 | P_SP_CV581_PT | Parameter - Setpoint PT660 for CV581 |  |  | P_LI660_max | Parameter - Maximum level | P_SP_CV603_LI670 | Parameter - Setpoint LI670 for CV603 |  |  | P_SP_CV601_FT | Parameter - Setpoint FT581 for CV601 | P_CV583 | Parameter : Order for Analog Valves |  |  |  |  | P_CV602 | Parameter - Order for Analog Valves | P_SP_CV653_TT | Parameter - Setpoint TT657 for CV653 | P_SP_CV581_PT | Parameter - Setpoint PT660 for CV581
DBD50 | Real | cParR8 | Real - Sequence parameter |  |  | P_CV603 | Parameter : Order for Analog Valves | P_CV680 | Parameter : Order for Analog Valves | [6 empty] | P_CV740 | Parameter : Order for Analog Valves | P_TT762_warm | Parameter : Temperature warm EV762 | P_Sec_Tt_Hig_LI680 | Parameter - High Temperature Security for Level | P_SP_CV600_FT | Parameter - Setpoint FT580 for CV600 | P_SP_CV601_FT | Parameter - Setpoint FT581 for CV601 |  |  | P_LI660_min | Parameter - Minimum level | P_LI660_max | Parameter - Maximum level |  |  | P_LI660_min | Parameter - Minimum level | P_CV680 | Parameter : Order for Analog Valves |  |  |  |  | P_QuenchMin_I | Parameter - Minimal current to react to quench | P_SP_CV653_FT | Parameter - Setpoint FT653 for CV653 | P_CV581 | Parameter - Order for Analog Valves
DBD54 | Real | cParR9 | Real - Sequence parameter |  |  | P_CV580 | Parameter : Order for Analog Valves | P_CV650 | Parameter : Order for Analog Valves | [6 empty] | P_TT740_warm | Parameter : Temperature warm EV740 | P_TT762_cold | Parameter : Temperature cold EV762 | P_Sec_Tt_Low_LT682 | Parameter - Low Temperature Security for Level | P_SP_CV580_PT | Parameter - Setpoint PT600 for CV580 | P_CV601 | Parameter - Order for Analog Valves |  |  | P_LI670_max | Parameter - Maximum level | P_LI660_min | Parameter - Minimum level |  |  | P_LI670_min | Parameter - Minimum level | P_TT685_max | Parameter - Maximum Temperature | [8 empty] | P_SP_CV583_PT | Parameter - Setpoint PT681 for CV583
DBD58 | Real | cParR10 | Real - Sequence parameter |  |  |  |  | P_CV651 | Parameter : Order for Analog Valves | [6 empty] | P_TT740_cold | Parameter : Temperature cold EV740 |  |  | P_Sec_Tt_Hig_LT682 | Parameter - High Temperature Security for Level | P_Tt_Cool_Down | Parameter - Temperature cool down | P_CV602 | Parameter - Order for Analog Valves |  |  | P_LI670_min | Parameter - Minimum level | P_LI670_max | Parameter - Maximum level |  |  |  |  | P_SP_CV581_PT | Parameter - Setpoint PT660 for CV581
DBD62 | Real | cParR11 | Real - Sequence parameter |  |  |  |  | P_CV652 | Parameter : Order for Analog Valves | [6 empty] | P_TT744_warm | Parameter : Temperature warm EV744 |  |  | P_Sec_Tt_Low_LT683 | Parameter - Low Temperature Security for Level | [8 empty] | P_LI670_min | Parameter - Minimum level |  |  |  |  | P_SP_CV583_PT | Parameter - Setpoint PT681 for CV583
DBD66 | Real | cParR12 | Real - Sequence parameter |  |  |  |  | P_CV653 | Parameter : Order for Analog Valves | [6 empty] | P_TT744_cold | Parameter : Temperature cold EV744 |  |  | P_Sec_Tt_Hig_LT683 | Parameter - High Temperature Security for Level | [8 empty] | P_PT660 | Parameter - Pressure for control |  |  |  |  | P_SP_CV581_FT | Parameter - Setpoint FT581 for CV581
DBD70 | Real | cParR13 | Real - Sequence parameter | [12 empty] | P_TT748_warm | Parameter : Temperature warm EV748 |  |  | P_Sec_LT600 | Parameter - Level Security | [8 empty] | P_PT584 | Parameter - Atmospheric pressure |  |  |  |  | P_SP_CV601_FT | Parameter - Setpoint FT583 for CV601
DBD74 | Real | cParR14 | Real - Sequence parameter | [12 empty] | P_TT748_cold | Parameter : Temperature cold EV748 |  |  | P_Sec_LI660 | Parameter - Level Security | [14 empty] | P_DeltaL | Parameter - DeltaL
DBD78 | Real | cParR15 | Real - Sequence parameter | [16 empty] | P_Sec_LI670 | Parameter - Level Security | [14 empty] | P_DeltaL_max | Parameter - DeltaL max
DBD82 | Real | cParR16 | Real - Sequence parameter | [16 empty] | P_Sec_LI680 | Parameter - Level Security | [14 empty] | P_dT_dt_max | Parameter - dT/dt max
Sequences
PLC -> EPICS
Type "Plc_to_Epi_Seq"
DBX0.0 | Bool | sActivate | Activate - State
DBX0.1 | Bool | sRun | Run - State
DBX0.2 | Bool | sPause | Pause - State
DBX0.3 | Bool | sFault | Fault - State
DBX0.4 | Bool | sStop | Stop - State
DBX0.5 | Bool | sStopping | Stopping - State
DBX0.6 | Bool | sCIok | Initials conditions ok
DBX0.7 | Bool | sCSok | Security conditions ok
DBX1.0 | Bool | sMsg_Display | Message - Display the message in SPV
DBX1.1 | Bool | Sque_Display | Question - Display the message in SPV
DBX2.0 | Bool | sFlt1 | Sequence Fault |  |  | Flt_Vaccum | Fault : Vaccum Alarm | Flt_Vaccum | Fault : Vaccum Alarm | Flt_Vaccum | Fault : Vaccum Alarm | [42 empty] | Flt_Pressure | Fault - He Circuits Pressure Alarm | Flt_Pressure | Fault - He Circuits Pressure Alarm
DBX2.1 | Bool | sFlt2 | Sequence Fault |  |  | Flt_HL_Vacuum | Fault : High level vacuum Alarm | Flt_HL_Vacuum | Fault : High level vacuum Alarm | Flt_HL_Vacuum | Fault : High level vacuum Alarm
DBX2.2 | Bool | sFlt3 | Sequence Fault |  |  | Flt_Pressure | Fault : Pressure Alarm | Flt_Pressure | Fault : Pressure Alarm | Flt_Pressure | Fault : Pressure Alarm
DBX2.3 | Bool | sFlt4 | Sequence Fault |  |  | Flt_LL_Pressure | Fault : Low level pressure Alarm | Flt_LL_Pressure | Fault : Low level pressure Alarm | Flt_LL_Pressure | Fault : Low level pressure Alarm
DBX2.4 | Bool | sFlt5 | Sequence Fault
DBX2.5 | Bool | sFlt6 | Sequence Fault
DBX2.6 | Bool | sCheckParam | Check Parameters |  |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para |  | Ctrl_Para
DBX2.7 | Bool | sCheckEquip | Check Equipment in manual mode |  |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run |  | Equip_Ok_Run
DBW4 | Int | sStep | Sequence Grafcet Step |  |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X |  | G7.G_X
DBW6 | Int | sStepTime | Temporisation of Sequence Grafcet Step |  |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7 |  | Tps_G7
DBW8 | Int | sStateI1 | Integer - State indicator |  |  | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display | Msg_Number | Message - Number of the message to display
DBW10 | Int | sStateI2 | Integer - State indicator |  |  | Cpt_Nb_Cycle | Counter : Actual Number of cycle | Cpt_Nb_Cycle | Counter : Actual Number of cycle | Cpt_Nb_Cycle | Counter : Actual Number of cycle
DBD12 | Real | sStateR1 | Real - State indicator
DBD16 | Real | sStateR2 | Real - State indicator
DBX20.0 | Bool | sParB1 | Bool - Sequence parameter | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters |  | Same as Epics to Plc commands parameters
DBX20.1 | Bool | sParB2 | Bool - Sequence parameter
DBX20.2 | Bool | sParB3 | Bool - Sequence parameter
DBX20.3 | Bool | sParB4 | Bool - Sequence parameter
DBX20.4 | Bool | sParB5 | Bool - Sequence parameter
DBX20.5 | Bool | sParB6 | Bool - Sequence parameter
DBX20.6 | Bool | sParB7 | Bool - Sequence parameter
DBX20.7 | Bool | sParB8 | Bool - Sequence parameter
DBW22 | Int | sParI1 | Integer - Sequence parameter
DBW24 | Int | sParI2 | Integer - Sequence parameter
DBW26 | Int | sParI3 | Integer - Sequence parameter
DBW28 | Int | sParI4 | Integer - Sequence parameter
DBW30 | Int | sParI5 | Integer - Sequence parameter
DBW32 | Int | sParI6 | Integer - Sequence parameter
DBW34 | Int | sParI7 | Integer - Sequence parameter
DBW36 | Int | sParI8 | Integer - Sequence parameter
DBW38 | Int | sInitCond | Sequence - Initials conditions
DBD40 | Real | sParR1 | Real - Sequence parameter
DBD44 | Real | sParR2 | Real - Sequence parameter
DBD48 | Real | sParR3 | Real - Sequence parameter
DBD52 | Real | sParR4 | Real - Sequence parameter
DBD56 | Real | sParR5 | Real - Sequence parameter
DBD60 | Real | sParR6 | Real - Sequence parameter
DBD64 | Real | sParR7 | Real - Sequence parameter
DBD68 | Real | sParR8 | Real - Sequence parameter
DBD72 | Real | sParR9 | Real - Sequence parameter
DBD76 | Real | sParR10 | Real - Sequence parameter
DBD80 | Real | sParR11 | Real - Sequence parameter
DBD84 | Real | sParR12 | Real - Sequence parameter
DBD88 | Real | sParR13 | Real - Sequence parameter
DBD92 | Real | sParR14 | Real - Sequence parameter
DBD96 | Real | sParR15 | Real - Sequence parameter
DBD100 | Real | sParR16 | Real - Sequence parameter
Note on E67: Maxime GUIGNERY: Appear when there is a message (with an acceptation command)
Note on E68: Maxime GUIGNERY: Appear if there is a question (with a yes/no answer)

## General
General |  |  |  | Gen
EPICS -> PLC |  |  |  | Parameter | Comment
Type "Epi_to_Plc_Gen"
DBX0.0 | Bool | cmdSetParam | Write parameters - Commands
DBX0.1 | Bool | CmdSetAck | Set General Acknoledge - Commands | ACK_GEN | General Acknowledge
DBX0.2 | Bool | CmdSpare3 | Spare - Commands | cmdVB_GB | ValveBox circuit : To GazBag
DBX0.3 | Bool | CmdSpare4 | Spare - Commands | cmdVB_Ka | ValveBox circuit : To Kaeser
DBX0.4 | Bool | CmdSpare5 | Spare - Commands | cmdCry4K_GB | Cryo4K circuit : To GazBag
DBX0.5 | Bool | CmdSpare6 | Spare - Commands | cmdCry4K_Ka | Cryo4K circuit : To Kaeser
DBX0.6 | Bool | CmdSpare7 | Spare - Commands | cmdMag4K_GB | Magnet4K circuit : To GazBag
DBX0.7 | Bool | CmdSpare8 | Spare - Commands | cmdMag4K_Ka | Magnet4K circuit : To Kaeser
DBX1.0 | Bool | cParB1 | Bool - Dialogue | CV_He_Liq_Cmd_Open_ACK | Open command for the CV_He_Liq acknowledged |  | CmdSetLocal
DBX1.1 | Bool | cParB2 | Bool - Dialogue | CV_He_Liq_Cmd_Close_ACK | Close command for the CV_He_Liq acknowledged |  | CmdSetRemote
DBX1.2 | Bool | cParB3 | Bool - Dialogue
DBX1.3 | Bool | cParB4 | Bool - Dialogue
DBX1.4 | Bool | cParB5 | Bool - Dialogue
DBX1.5 | Bool | cParB6 | Bool - Dialogue
DBX1.6 | Bool | cParB7 | Bool - Dialogue
DBX1.7 | Bool | cParB8 | Bool - Dialogue
DBW2 | Int | cParI1 | Integer - Dialogue | HBcounter | HeartBeat counter (updates at least every 10 s)
DBW4 | Int | cParI2 | Integer - Dialogue
DBW6 | Int | cParI3 | Integer - Dialogue
DBW8 | Int | cParI4 | Integer - Dialogue
DBW10 | Int | cParI5 | Integer - Dialogue
DBW12 | Int | cParI6 | Integer - Dialogue
DBW14 | Int | cParI7 | Integer - Dialogue
DBW16 | Int | cParI8 | Integer - Dialogue
DBW18 | Int | cParI9 | Integer - Dialogue
DBD20 | Real | cParR1 | Real - Dialogue | 2KPumps-Freq | Mean revol. Freq. of all 2K pumps Hz
DBD24 | Real | cParR2 | Real - Dialogue
DBD28 | Real | cParR3 | Real - Dialogue
DBD32 | Real | cParR4 | Real - Dialogue
DBD36 | Real | cParR5 | Real - Dialogue
DBD40 | Real | cParR6 | Real - Dialogue
DBD44 | Real | cParR7 | Real - Dialogue
DBD48 | Real | cParR8 | Real - Dialogue
DBD52 | Real | cParR9 | Real - Dialogue
DBD56 | Real | cParR10 | Real - Dialogue
DBD60 | Real | cParR11 | Real - Dialogue
DBD64 | Real | cParR12 | Real - Dialogue
DBD68 | Real | cParR13 | Real - Dialogue
DBD72 | Real | cParR14 | Real - Dialogue
DBD76 | Real | cParR15 | Real - Dialogue
DBD80 | Real | cParR16 | Real - Dialogue
General
PLC -> EPICS
Type "Plc_to_Epi_Gen"
DBX0.0 | Bool |  |  | sLocal | false - EPICS rules, true - WinCC is in charge
DBX0.1 | Bool |  |  | CV5203_OpenReq | Request to keep CV5203 open (if true)
DBX0.2 | Bool
DBX0.3 | Bool
DBX0.4 | Bool
DBX0.5 | Bool
DBX0.6 | Bool
DBX0.7 | Bool
DBX1.0 | Bool | sParB1 | Bool - Dialogue | CV_He_Liq_Cmd_Open | Open command for the CV_He_Liq | <-Removed
DBX1.1 | Bool | sParB2 | Bool - Dialogue | CV_He_Liq_Cmd_Close | Close command for the CV_He_Liq | <-Removed
DBX1.2 | Bool | sParB3 | Bool - Dialogue
DBX1.3 | Bool | sParB4 | Bool - Dialogue
DBX1.4 | Bool | sParB5 | Bool - Dialogue
DBX1.5 | Bool | sParB6 | Bool - Dialogue
DBX1.6 | Bool | sParB7 | Bool - Dialogue
DBX1.7 | Bool | sParB8 | Bool - Dialogue
DBW2 | Int | sParI1 | Integer - Dialogue | Hbcounter_recopy | HeartBeat counter (recopy of the send value)
DBW4 | Int | sParI2 | Integer - Dialogue | stateVB | 0=Nothing 1=Kaeser 2=GasBag 3=Kaeser in progress 4=GasBas in progress
DBW6 | Int | sParI3 | Integer - Dialogue | stateCry4K | 0=Nothing 1=Kaeser 2=GasBag 3=Kaeser in progress 4=GasBas in progress
DBW8 | Int | sParI4 | Integer - Dialogue | stateMag4K | 0=Nothing 1=Kaeser 2=GasBag 3=Kaeser in progress 4=GasBas in progress
DBW10 | Int | sParI5 | Integer - Dialogue
DBW12 | Int | sParI6 | Integer - Dialogue
DBW14 | Int | sParI7 | Integer - Dialogue
DBW16 | Int | sParI8 | Integer - Dialogue
DBW18 | Int | sParI9 | Integer - Dialogue
DBD20 | Real | sParR1 | Real - Dialogue
DBD24 | Real | sParR2 | Real - Dialogue
DBD28 | Real | sParR3 | Real - Dialogue
DBD32 | Real | sParR4 | Real - Dialogue
DBD36 | Real | sParR5 | Real - Dialogue
DBD40 | Real | sParR6 | Real - Dialogue
DBD44 | Real | sParR7 | Real - Dialogue
DBD48 | Real | sParR8 | Real - Dialogue
DBD52 | Real | sParR9 | Real - Dialogue
DBD56 | Real | sParR10 | Real - Dialogue
DBD60 | Real | sParR11 | Real - Dialogue
DBD64 | Real | sParR12 | Real - Dialogue
DBD68 | Real | sParR13 | Real - Dialogue
DBD72 | Real | sParR14 | Real - Dialogue
DBD76 | Real | sParR15 | Real - Dialogue
DBD80 | Real | sParR16 | Real - Dialogue
Note on J7: Maxime GUIGNERY: Changing circuit for Re-Heater. SET the commands and it will be reset by API
Note on J8: Maxime GUIGNERY: Changing circuit for Re-Heater. SET the commands and it will be reset by API
Note on J9: Maxime GUIGNERY: Changing circuit for Re-Heater. SET the commands and it will be reset by API
Note on J10: Maxime GUIGNERY: Changing circuit for Re-Heater. SET the commands and it will be reset by API
Note on J11: Maxime GUIGNERY: Changing circuit for Re-Heater. SET the commands and it will be reset by API
Note on J12: Maxime GUIGNERY: Changing circuit for Re-Heater. SET the commands and it will be reset by API
Note on J14: Konrad Gajewski: This bitt will go high for 0.5 s when the open command is received by EPICS. The PLC program should then reset the command bit CV_He_Liq_Cmd_Open
Note on L14: Konrad Gajewski: Not implemented yet
Note on J15: Konrad Gajewski: This bitt will go high for 0.5 s when the close command is received by EPICS. The PLC program should then reset the command bit CV_He_Liq_Cmd_Close
Note on L15: Konrad Gajewski: Not implemented yet
Note on I23: Konrad Gajewski: This bit is not needed, we agreed that all communication from EPICS will come from horizontal cryostat via PLC<->PLC data block MG : I don't agree. We have a communication between EPICS and the Vertical Cryostat API, and I wust watch this with a HeartBit coutner
Note on J33: Maxime GUIGNERY: I need this information for my grafect ("pumps stopped"). This info is not available in the Horizontal Cryostat API

## Parameters
Real Parameters |  |  |  | SQ8 : Additional parameters |  | SQ13_CV582_Press |  | SQ13_CV582_Press |  | SQ15 : Additional parameters |  | SQ17_CV582_Press |  | SQ17_CV582_Press
EPICS -> PLC |  |  |  | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment | Parameter | Comment
Type "Epi_to_Plc_ParR"
DBD0 | Real | cParR0 | Real - Dialogue | P_Sec_LT682 | Parameter - Level Security | P_CV582_Press.PT00 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg03 | Parameter -Order for CV582 | P_SP_TT680 | Parameter - Temperature setpoint | P_CV582_Press.PT00 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg03 | Parameter -Order for CV582
DBD4 | Real | cParR1 | Real - Dialogue | P_Sec_LT683 | Parameter - Level Security | P_CV582_Press.PT01 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg04 | Parameter -Order for CV582 | P_SP_LT683 | Parameter - Level setpoint | P_CV582_Press.PT01 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg04 | Parameter -Order for CV582
DBD8 | Real | cParR2 | Real - Dialogue |  |  | P_CV582_Press.PT02 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg05 | Parameter -Order for CV582 | P_SP_CV602_LT | Parameter - Setpoint LT682 for CV602 | P_CV582_Press.PT02 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg05 | Parameter -Order for CV582
DBD12 | Real | cParR3 | Real - Dialogue |  |  | P_CV582_Press.PT03 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg06 | Parameter -Order for CV582 |  |  | P_CV582_Press.PT03 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg06 | Parameter -Order for CV582
DBD16 | Real | cParR4 | Real - Dialogue |  |  | P_CV582_Press.PT04 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg07 | Parameter -Order for CV582 |  |  | P_CV582_Press.PT04 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg07 | Parameter -Order for CV582
DBD20 | Real | cParR5 | Real - Dialogue |  |  | P_CV582_Press.PT05 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg08 | Parameter -Order for CV582 |  |  | P_CV582_Press.PT05 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg08 | Parameter -Order for CV582
DBD24 | Real | cParR6 | Real - Dialogue |  |  | P_CV582_Press.PT06 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg09 | Parameter -Order for CV582 |  |  | P_CV582_Press.PT06 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg09 | Parameter -Order for CV582
DBD28 | Real | cParR7 | Real - Dialogue |  |  | P_CV582_Press.PT07 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg10 | Parameter -Order for CV582 |  |  | P_CV582_Press.PT07 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg10 | Parameter -Order for CV582
DBD32 | Real | cParR8 | Real - Dialogue |  |  | P_CV582_Press.PT08 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg11 | Parameter -Order for CV582 |  |  | P_CV582_Press.PT08 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg11 | Parameter -Order for CV582
DBD36 | Real | cParR9 | Real - Dialogue |  |  | P_CV582_Press.PT09 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg12 | Parameter -Order for CV582 |  |  | P_CV582_Press.PT09 | Parameter - Pressure target for CV582 | P_CV582_Press.Csg12 | Parameter -Order for CV582
DBD40 | Real | cParR10 | Real - Dialogue |  |  | P_CV582_Press.PT10 | Parameter - Pressure target for CV582 |  |  |  |  | P_CV582_Press.PT10 | Parameter - Pressure target for CV582
DBD44 | Real | cParR11 | Real - Dialogue |  |  | P_CV582_Press.PT11 | Parameter - Pressure target for CV582 |  |  |  |  | P_CV582_Press.PT11 | Parameter - Pressure target for CV582
DBD48 | Real | cParR12 | Real - Dialogue |  |  | P_CV582_Press.PT12 | Parameter - Pressure target for CV582 |  |  |  |  | P_CV582_Press.PT12 | Parameter - Pressure target for CV582
DBD52 | Real | cParR13 | Real - Dialogue |  |  | P_CV582_Press.Csg00 | Parameter -Order for CV582 |  |  |  |  | P_CV582_Press.Csg00 | Parameter -Order for CV582
DBD56 | Real | cParR14 | Real - Dialogue |  |  | P_CV582_Press.Csg01 | Parameter -Order for CV582 |  |  |  |  | P_CV582_Press.Csg01 | Parameter -Order for CV582
DBD60 | Real | cParR15 | Real - Dialogue |  |  | P_CV582_Press.Csg02 | Parameter -Order for CV582 |  |  |  |  | P_CV582_Press.Csg02 | Parameter -Order for CV582
Real Parameters
PLC -> EPICS
Type "Plc_to_Epi_ParR"
DBD0 | Real | sParR0 | Real - Dialogue
DBD4 | Real | sParR1 | Real - Dialogue
DBD8 | Real | sParR2 | Real - Dialogue
DBD12 | Real | sParR3 | Real - Dialogue
DBD16 | Real | sParR4 | Real - Dialogue
DBD20 | Real | sParR5 | Real - Dialogue
DBD24 | Real | sParR6 | Real - Dialogue
DBD28 | Real | sParR7 | Real - Dialogue
DBD32 | Real | sParR8 | Real - Dialogue
DBD36 | Real | sParR9 | Real - Dialogue

## Alarm
Bool Alarm
PLC -> Epics
Type "Plc_to_Epi_Alarm"
DBX0.0 | Bool | Al1 | Alarm
DBX0.1 | Bool | Al2 | Alarm
DBX0.2 | Bool | Al3 | Alarm
DBX0.3 | Bool | Al4 | Alarm
DBX0.4 | Bool | Al5 | Alarm
DBX0.5 | Bool | Al6 | Alarm
DBX0.6 | Bool | Al7 | Alarm
DBX0.7 | Bool | Al8 | Alarm
DBX1.0 | Bool | Al9 | Alarm
DBX1.1 | Bool | Al10 | Alarm
DBX1.2 | Bool | Al11 | Alarm
DBX1.3 | Bool | Al12 | Alarm
DBX1.4 | Bool | Al13 | Alarm
DBX1.5 | Bool | Al14 | Alarm
DBX1.6 | Bool | Al15 | Alarm
DBX1.7 | Bool | Al16 | Alarm
DBX2.0 | Bool | Al17 | Alarm
DBX2.1 | Bool | Al18 | Alarm
DBX2.2 | Bool | Al19 | Alarm
DBX2.3 | Bool | Al20 | Alarm
DBX2.4 | Bool | Al21 | Alarm
DBX2.5 | Bool | Al22 | Alarm
DBX2.6 | Bool | Al23 | Alarm
DBX2.7 | Bool | Al24 | Alarm
DBX3.0 | Bool | Al25 | Alarm
DBX3.1 | Bool | Al26 | Alarm
DBX3.2 | Bool | Al27 | Alarm
DBX3.3 | Bool | Al28 | Alarm
DBX3.4 | Bool | Al29 | Alarm
DBX3.5 | Bool | Al30 | Alarm
DBX3.6 | Bool | Al31 | Alarm
DBX3.7 | Bool | Al32 | Alarm
DBX4.0 | Bool | Al33 | Alarm
DBX4.1 | Bool | Al34 | Alarm
DBX4.2 | Bool | Al35 | Alarm
DBX4.3 | Bool | Al36 | Alarm
DBX4.4 | Bool | Al37 | Alarm
DBX4.5 | Bool | Al38 | Alarm
DBX4.6 | Bool | Al39 | Alarm
DBX4.7 | Bool | Al40 | Alarm
DBX5.0 | Bool | Al41 | Alarm
DBX5.1 | Bool | Al42 | Alarm
DBX5.2 | Bool | Al43 | Alarm
DBX5.3 | Bool | Al44 | Alarm
DBX5.4 | Bool | Al45 | Alarm
DBX5.5 | Bool | Al46 | Alarm
DBX5.6 | Bool | Al47 | Alarm
DBX5.7 | Bool | Al48 | Alarm
DBX6.0 | Bool | Al49 | Alarm
DBX6.1 | Bool | Al50 | Alarm
DBX6.2 | Bool | Al51 | Alarm
DBX6.3 | Bool | Al52 | Alarm
DBX6.4 | Bool | Al53 | Alarm
DBX6.5 | Bool | Al54 | Alarm
DBX6.6 | Bool | Al55 | Alarm
DBX6.7 | Bool | Al56 | Alarm
DBX7.0 | Bool | Al57 | Alarm
DBX7.1 | Bool | Al58 | Alarm
DBX7.2 | Bool | Al59 | Alarm
DBX7.3 | Bool | Al60 | Alarm
DBX7.4 | Bool | Al61 | Alarm
DBX7.5 | Bool | Al62 | Alarm
DBX7.6 | Bool | Al63 | Alarm
DBX7.7 | Bool | Al64 | Alarm
DBX8.0 | Bool | Al65 | Alarm
DBX8.1 | Bool | Al66 | Alarm
DBX8.2 | Bool | Al67 | Alarm
DBX8.3 | Bool | Al68 | Alarm
DBX8.4 | Bool | Al69 | Alarm
DBX8.5 | Bool | Al70 | Alarm
DBX8.6 | Bool | Al71 | Alarm
DBX8.7 | Bool | Al72 | Alarm
DBX9.0 | Bool | Al73 | Alarm
DBX9.1 | Bool | Al74 | Alarm
DBX9.2 | Bool | Al75 | Alarm
DBX9.3 | Bool | Al76 | Alarm
DBX9.4 | Bool | Al77 | Alarm
DBX9.5 | Bool | Al78 | Alarm
DBX9.6 | Bool | Al79 | Alarm
DBX9.7 | Bool | Al80 | Alarm