## GENERAL
Add the text od initial conditions to all sequences.
Add PT584 on GUI
In Windows it can be impossible to enter decimal point - it depends on the language settings. Alternatively use , (comma)
PID LIC660A. LIC660 does not show the PID parameters in Epics - it's OK in WinCC. Reported by email to ISII-Tech and CD on 2019-03-11
Sensors TT607/617 and TT606/616 must change the place with each other on the synoptic screens
Change the label on the SCHe opi - control valve is CV380 (not CV301)
Note on B2: Author: Done on 2019-03-11
Note on B3: Author: Done on 2019-03-11
Note on B9: Author: Done on 2019-01-13
Note on B10: Author: Done on 2019-03-11

## InitialConditions
Initial conditions
CI |  | Seq 1 | Seq 2 | Seq 3 | Seq 4 | Seq 5 | Seq 6 | Seq 7 | Seq 8 | Seq 9 | Seq 10 | Seq 11 | Seq 12 | Seq 13 | Seq 14 | Seq 15 | Seq 16 | Seq 17 | Seq 18 | Seq 19 | Seq 20 | Seq 21 | Seq 22 | Seq 23 | Seq 24 | Seq 25
0
1 | Sequences from 5 to 20 must be stopped | bar: Seq 1 to Seq 3
2 | Sequence 21 must be stopped | bar: Seq 5
3 | Sequence 22 must be stopped | bar: Seq 6
4 | Sequence 23 must be stopped | bar: Seq 7
5 | Sequences from 1 to 3 must be stopped | bar: Seq 9 to Seq 10; Seq 12 to Seq 23
6 | Sequence 6 must be running | bar: Seq 9
7 | Sequences from 12 to 13 must be stopped | bar: Seq 10
8 | Sequence 3 must be stopped | bar: Seq 11
9 | Sequences 10 and 13 must be stopped | bar: Seq 12
10 | Sequences 10 and 12 must be stopped | bar: Seq 13
11 | Sequences from 10 to 13 must be stopped | bar: Seq 14
12 | Sequences from 16 to 18 must be stopped | bar: Seq 15
13 | Sequences 15, 17 and 18 must be stopped | bar: Seq 16
14 | Sequences 15 and 16 must be stopped | bar: Seq 17 to Seq 18
15 | Sequence 17 must be running | bar: Seq 18
16 | Sequences 10, 12, 13 and 14 must be stopped | bar: Seq 20
17 | Sequences from 15 to 19 must be stopped | bar: Seq 20
18 | Sequences 5 and 9 must be stopped | bar: Seq 21
19 | Sequences 6 and 7 must be stopped | bar: Seq 22 to Seq 24
20 | Sequences from 10 to 20 must be stopped | bar: Seq 22 to Seq 24
21 | Sequence 1 must be stopped | bar: Seq 5
22 | Sequences 2 and 3 must be stopped | bar: Seq 6 to Seq 7
23 | Sequences 5 and 8 must be running | bar: Seq 9
24 | Sequences 6 and 8 must be running | bar: Seq 10; Seq 12 to Seq 18
25 | Sequence 8 must be running | bar: Seq 20 to Seq 23
26 | Seq. 16 step 4 or Seq. 17 step 20 must be running | bar: Seq 4
27
28
29
30 | Liquid or Magnet insert must be selected | bar: Seq 6; Seq 20
31 | Vacuum insert must be selected | bar: Seq 7
32 | Liquid or Vacuum insert must be selected | bar: Seq 10; Seq 12 to Seq 14
33 | Magnet insert must be selected | bar: Seq 15 to Seq 19
34
35
36
37
38
Implemented in PLC GERSEMI_2020_02_20

## SQ1
Sequence 1: Valve Box, conditioning He circuits
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Prepare for purging
5
6 | Start the pumping
7
8 | Pumping
9
10 | Leak test at low pressure
11
12 | Flushing with GHe
13
14 | Leak test at high pressure
15
16 | Valve Box circuits isolated |  | Waiting for valve FV600 to close
17
18 | Helium conditioning stopped
19
20 | Pump stopped
21
22 | Vacuum alarm |  | Waiting for acknowledge ACK_GENE
23
24 | High level vacuum alarm |  | Waiting for acknowledge ACK_GENE
25
26 | Waiting for the operator's answer | 1 | Do you want to stop the conditioning (Yes/No)?
27
28 | Waiting for the operator's answer | 2 | Do you want to keep the lines under pressure (Yes/No)?
29
30 | Circuits closed |  | Waiting for FV090 to close
31
32 | Flushing with GHe
33
34 | Waiting for the operator's answer | 4 | What message? Waits only for Yes
35
36 | Pressure alarm |  | Waiting for acknowledge ACK_GENE
37
38 | Low level pressure alarm |  | Waiting for acknowledge ACK_GENE
39
40 | Waiting for the operator's answer | 3 | Do you want to stop the conditioning (Yes/No)?
PT090 shows invalid link alarm - correct - sensor not connected? Input value 0x7fff
Change the panel labels PT552 PT551 to the right vacuumeters PT580
FV584 open during the purge - should be closed but this is true only for the simulator. For the real cryostat it doesn't matter
Note on B48: Author: Done 2019-02-12

## SQ2
Sequence 2: Cryostat, conditioning He circuits
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Prepare for purging
5
6 | Start the pumping
7
8 | Pumping
9
10 | Leak test at low pressure
11
12 | Flushing with GHe
13
14 | Leak test at high pressure
15
16 | Cryostat circuits isolated |  | Waiting for valve FV660 to close
17
18 | Helium conditioning stopped
19
20 | Pump stopped |  | Waiting for pump P090 to stop
21
22 | Vacuum alarm |  | Waiting for acknowledge ACK_GENE
23
24 | High level vacuum alarm |  | Waiting for acknowledge ACK_GENE
25
26 | Waiting for the operator's answer | 1 | Do you want to stop the conditioning (Yes/No)?
27
28 | Waiting for the operator's answer | 2 | Do you want to keep the lines under pressure (Yes/No)?
29
30 | Circuits closed |  | Waiting for FV090 to close
31
32 | Flushing with GHe
33
34 | Waiting for the operator's answer | 4 | What message? Waits only for Yes
35
36 | Pressure alarm |  | Waiting for acknowledge ACK_GENE
37
38 | Low level pressure alarm |  | Waiting for acknowledge ACK_GENE
39
40 | Waiting for the operator's answer | 3 | Do you want to stop the conditioning (Yes/No)?
Change the panel labels PT552 PT551 to the right vacuumeter PT581
Add the PT581 read-out
Note on B49: Author: Done 2019-03-12
Note on B50: Author: Done 2019-03-12

## SQ3
Sequence 3: SCHe, conditioning He circuits
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Prepare for purging
5
6 | Start the pumping
7
8 | Pumping
9
10 | Leak test at low pressure
11
12 | Flushing with GHe
13
14 | Leak test at high pressure
15
16 | CSHe circuits isolated |  | Waiting for valve FV380 to close
17
18 | Helium conditioning stopped
19
20 | Pump stopped |  | Waiting for pump P090 to stop
21
22 | Vacuum alarm |  | Waiting for acknowledge ACK_GENE
23
24 | High level vacuum alarm |  | Waiting for acknowledge ACK_GENE
25
26 | Waiting for the operator's answer | 1 | Do you want to stop the conditioning (Yes/No)?
27
28 | Waiting for the operator's answer | 2 | Do you want to keep the lines under pressure (Yes/No)?
29
30 | Circuits closed |  | Waiting for FV090 to close
31
32 | Flushing with GHe
33
34 | Waiting for the operator's answer | 4 | What message? Waits only for Yes
35
36 | Pressure alarm |  | Waiting for acknowledge ACK_GENE
37
38 | Low level pressure alarm |  | Waiting for acknowledge ACK_GENE
39
40 | Waiting for the operator's answer | 3 | Do you want to stop the conditioning (Yes/No)?
PT381 goes down only down to 35 mbar -it's not possible to achieve lower pressure
PT380 goes down only to 20 mbar
Add the read-out of PT381 to the panel
Note on B50: Author: Done 2019-03-12

## SQ4
Sequence 4: Magnet insert, HV tests
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Waiting for Yes/No | 1 | Wait for confirmation to start the tests.
5
6 | Are the cables disconnected? - waiting for "Yes" | 2 | Set relevant PVs in the Sim mode, turn off actuators for the valves and heaters. Operator disconnects the cable and confirms it by pressing Yes
7
8 | HV test (waiting for stop) | 3 | Control the flow/pressure. Waiting for "Stop" after reconnecting the cables
9
10 | Restoring connection to PVs |  | Resets the Sim mode, rstores the proper control of the heaters and valves. Automatic transition to 12 after 5 s
11
12 | Gracefull transition to normal operation |  | When done exit the sequence
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27

## SQ5
Sequence 5: Valve Box thermal shield cooling
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Starting LN2 flow |  | Waiting for TT704 or TT706 to go below "Coold down temp."
5
6 | LN2 circulation
7
8 | Closing filling valve |  | Stopping, waiting for CV700 to close
Add the temperature read-outs to the panel
Add the reminder to close the LN2 valve when stopping the sequence
Note on B16: Author: Done 2019-03-12
Note on B17: Author: Done on 2019-03-11

## SQ6
Sequence 6: Cryostat thermal shield cooling
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Starting LN2 flow |  | Waiting for TT752 orr TT749 to go below "Coold down temp."
5
6 | LN2 circulation
7
8 | Closing filling valve |  | Stopping, waiting for CV740 to close
Add the reminder to close the LN2 valve when stopping the sequence
Add temperature read-outs to the panel
Note on B16: Author: Done on 2019-03-11
Note on B17: Author: Done 2019-03-12

## SQ7
Sequence 7: Vacuum insert thermal shield cooling
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Starting LN2 flow |  | Waiting for TT746 orr TT764 to go below "Coold down temp."
5
6 | LN2 circulation
Add temperature read-out
Note on B14: Author: Done 2019-03-12

## SQ8
Sequence 8: LHe level measurements
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Doing measurements
Add data read-outs
Note on B12: Author: Done 2019-03-12

## SQ9
Sequence 9: Valve Box cooling & controlling level in 4K tank (Revised 2021-04-21)
Warning flow SQ9_FT580 not available in epics. Maybe we should create such a bit in EPICS DB
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Waiting for "Yes" | 1 | Have you chosen the recovery circuit for the valve Box?
5
6 | Waiting for local Ack |  | Select the proper Lhe source and press "Accept". Goto step 32 (Liq & RegOn), 41 (Liq & Intermittent), 7 (Dwr). Can be stopped.
7
7 | Waiting for Yes | 3 | Waiting for Yes (Is dewar connected?) Then goto 8 (RegOn), 13 (Intermittent).
8 | Prepare to regulate (Dewar mode) |  | Waiting for CV580 to be >= CV580 parameter in the panel, then goto 10
9
10 | Regulation mode (Dewar mode) |  | Waits for Stop Dewar and goto 12 or switch to intermittent and goto 11
11
11 |  |  | Wait for CV600 to close and LT600<P_LT600_min then goto 16 or switch to RegOn and goto 10
12 | Dewar isolated (Dewar mode) |  | Waiting for FV602 to close then goto 24
13
13 | Dewar mode, Intermittent |  | Waiting for LT600 below P_LT600_min, then goto 14
14 | Preparation to fill (Dewar mode) |  | Waiting for FV602 to open then goto 16
15
16 | Cool down TL L010 (Dewar mode) |  | Waiting for TT602 or TT614 to go below TT Cool-down then goto 18
17
18 | 4K tank filling (Dewar mode) |  | Waiting for LT600 > LT600 Max then goto 20 or changing to PID mode anf goto 10
19
20 | End of filling (Dewar mode) |  | Waiting for LT600 < LT600 Min in Intermittent mode then goto 16 or changing to PID mode then goto 10 or stop Dewar or stop Seq9 and goto 22
21
22 | Dewar isolated (Dewar mode) |  | Waiting for FV602 to close then goto 24
23
24 | Waiting for the operator Yes/No | 2 | Do you want to close the valve of the Dewar? Yes - goto 26; No - goto 28
25
26 | Dewar valve closed |  | Waiting for CV590 to close or in state_stopping then goto 28
27
28 | Avoid closed volume |  | Waiting for CV600 to close, goto 30 and reset CV600 (mem) regulation
29
30 | 4K tank outgasing (Liquefier mode) |  | In Intermittent mode goto 41, in Reg mode goto 32 or Stop and goto 0
31
32 | Preparation to regulate |  | Waiting for CV580 to be >= CV580 parameter in the panel and CV5203 open (from HNOSS data) and CV5203 PercOut = 100% and Not HNOSS comm error then goto 34
33
34 | Regulation mode (Liquefier mode) |  | Waiting for Stop Liquefier or stopping Seq9 then goto 36 or switch to intermittent mode and goto 35
35
35 | Intermittent mode (Liquefier mode) |  | Wait for CV600 to close and LT600<P_LT600_min then goto42 or switch to RegOn and goto 34
36 | Liquefier valve closing |  | Not HNOSS com error and CV5203 closed (from HNOSS data) and CV5203 PercOut <= 0 then goto 38
37
38 | Avoid closed volume |  | Waiting for CV600 to close then goto 40
39
40 | 4K tank outgasing (Dewar mode) |  | Goto 7, if in intermittent mode set FV601 mem, When stopping goto 0
41
41 | Wait for level to go below min. |  | Waiting for LT600 < P_LT600_min then goto 42
42 | Cool down TL L010 |  | Wait for TT602 or TT614 to go below TT Cool-down and CV5203 pERCoUT = 100 and HNOSS comm OK then goto 44. When stopping goto 46
43
44 | 4K tank filling (Liquefier mode) |  | Waiting for LT600 > LT600 Max then goto 46 or ait for changing to PID mode and goto 34. When stopping goto 46.
45
46 | End of filling (Liquefier mode) |  | Waiting for stop Seq9 or Stop Liquefier mode then goto 48 or and Waiting for LT600 < LT600 Min in Intermittent mode and goto 42 or changing to PID mode and goto 34. When stopping goto 48
47
48 | Liquefier valve closing |  | HNOSS comm OK and CV5203 status closed and CV5203 PercOut <= 0 then goto 38
Tested transitions intermittent <-> PID mode - OK
Define name of the states (new and modified)
Maybe the comm to HNOSS OK should be added in initial conditions
Note on D55: Author: Stopping has been fixed (added) on 2021-04-21
Note on B62: Author: Done 2019-03-12

## SQ10
Sequence 10: Cavity cooling (revised 2019-03-08)
Warning flow SQ10_FT580 not available in epics. Maybe we should create such a bit in EPICS DB. Why in this sequenc a SP FIC581 is used for the limit?
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Waiting for "Yes" | 1 | After Yes goto 8
5
6 | NOT USED
7
8 | Cooling cavity |  | Waiting for LI670 > LI670 Max or LI660 > LI660 Max then goto 10
9
10 | End of cool-down |  | Wait for CV601 to be closed (actualy CV601 set-point to be 0) then goto 12
11
12 | Prepare to regulate |  | In Intermittent mode wait for LT660 < LT660 Min or LT670 < LT670 Min then goto 16 or change to PID mode and goto 14
13
14 | Regulation mode PID |  | If changed to intermittent mode goto 15
15 |  |  | Wait for LT660 < LT660 Min or LT670 < LT670 Min then goto 16 or change to PID mode and goto 14
16 | Cryostat filling |  | Waiting for LT660 > LT660 Max or LT670 > LT670 Max then goto 18 or changing to PID mode (goto 14)
17
18 | End of filling |  | In Intermittent mode wait for LT660 < LT660 Min or LT670 < LT670 Min then goto 16 or change to PID mode and goto 14
19
20 | Stop cooling |  | Wait fot CV602 to be closed (Out_sp = 0) then stop
Tested transitions intermittent <-> PID mode - OK
Change the name of step 14 to PID mode
Define name for state 15
Note on B29: Author: Done 2019-03-13
Note on B30: Author: Done2019-03-13

## SQ11
Sequence 11: SCHe operation
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Open circuit |  | Delaying for "Time open circ." parameter
5
6 | Start compressor |  | Waiting for compressor to start and then delaying for "Time start compressor" parameter
7
8 | Regulation |  | Waiting for Stopping
9
10 | Stop SCHe cooling |  | Wait for compressor to be off
11
12 | Close circuit |  | Wait for CV380 to be closed
No signal from the compressor I9.6 - connected I3.1 pin 15 to +24V - can be disconnected by means of the terminal block switch
The flow regulation doesn't work very well

## SQ12
Sequence 12: Cavity, 4K operation (Revised 2019-02-26)
Warning flow SQ12_FT580 not available in epics. Maybe we should create such a bit in EPICS DB. Why in this sequenc a SP FIC581 is used for the limit?
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Filling ready (Intermittent mode) |  | Wait for LI660 < LI660 Min or LI670 < LI670 Min then goto 8 or switching to PID mode and goto 6
5
6 | Regulation (PID) |  | Wait for switching to Intermittend mode then goto 7
7 | Intermittent mode |  | Wait for (LI660 < LI660 Min or LI670 < LI670 Min) then goto 8 or switch to PID and goto 6
8 | Start filling |  | Wait for LI660 > LI660 Max or LI670 > LI670 Max then goto 10 or switching to PID mode and goto 6
9
10 | End of filling |  | In Intermittent mode: Wait for LI660 < LI660 Min or LI670 < LI670 Min then goto 8 or switch to PID mode and goto 6
11
12 | Stop cooling |  | Wait for (FV642 Liquid insert) or FV643 (Vacuum insert)) and CV602 to be closed
Add text for step 7
Note on B20: Author: Done2019-03-13

## SQ13
Sequence 13: Cavity, 2K operation (Rev. 2019-02-26)
All initial conditions masked, Should be added HNOSS commOK condition when using FV551, FV554, FV555 & FV556
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Waiting for Yes/No answer | 1 | You are starting the 2K pumps, do you want to continue? If No - stop the sequence If Yes: wait for FV551 to close and (LI660 >= LI660 Min or LI670 >= LI670 Min) then goto 8 or wait for FV551 to close and (LI660 < LI660 Min or LI670 < LI670 Min) then goto 6
5
6 | Waiting for Yes/No answer | 2 | The 2K tank is not filled, do you want to continue? If No - stop the sequence, if Yes - go to step 8
7
8 | Cryostat connected to the recovery |  | Waiting for CV581 >= CV581 parameter then goto 10
9
10 | Prepare 2 K pump |  | Wait for FV554 to close and FV555 to open then goto 12
11
12 | Starting pumps, Waiting for Yes | 4 | Waiting for Yes, then goto 14
13
14 | Isolating 2K tank |  | Waiting for CV581 to be closed then goto 16
15
16 | 2K circuit closed |  | Waiting for FV581 and FV584 to be closed then Start SQ13A and goto 18
17
18 | Pumping 2 K tank |  | Wait until PT660 is close to P_SP_CV582_PT660 (EPICS: SP_PIC660) within tollerances in "COMM_PARAM".SQ13.Low_Tol_PT660 and "COMM_PARAM".SQ13.High_Tol_PT660 then goto 20 Check - it was possible to stop the sequence
19
20 | 2K tank pressure regulated |  | Wait for stopping then goto 22 and stop Seq13A or wait for decreasing SP PIC660 and goto 18.
21
22 | Stop pumping |  | Wait for SQ13 stopping and FV582 to be closed then goto 24
23
24 | Pressure control | 3 | Wait for SQ13 stopping andDB_SQ13.pump2K_stopped then goto 26
25
26 | Cryostat connected to the recovery |  | Wait for PT584 go above sequence parameter PT584 then goto 28
27
28 | Stop filling line |  | Wait for Seq13_Mini be in state 2 and CV581 >= P_CV581 then stop Seq13 and Seq13_Mini
There is message 3 in step 24 but it is not used
Change the name of state 12: Waiting for 2k pumps to be ready for operation
Define text for Question 4 to: Press Yes to continue
After stopping the sequence it stacked in state 28 because the Seq13A was not running but we have been doing manual tests that could have infuenced the sequence
CV582 - tried to set the Reg ON in manual mode - didn't work (tried with the valve itself in Auto and Man mode)
Add a hardware reading of the closed position and check that CV582 is closed before doing transition to state 18 - pumping 2K tank
In the state 18 the program does not open CV582 according to the table
Tested switching Vbox to Kaser and gas back in state 20 - worked ok.
Tested changing the pressure setpoint in both directions - worked ok
Note on B36: Author: Fixed in version 2019_03_11
Note on B37: Author: Fixed 2019-03-13
Note on B38: Author: Fixed 2019-03-13
Note on B40: Author: Fixed by ISII-Tech
Note on B41: Author: This is difficult to fix in the current implementation of the vale control - it's not done via CONT_C function but directly on the control variable. The problem exist for all CV that can be controlled by a PID
Note on B42: Author: It's possible to do. We can do it ourselves later on.
Note on B43: Author: Fixed by ISII-Tech

## SQ13A
Sequence 13A: Cavity, 2K operation - subsequence of SQ13 (Rev 2019-02-26)
Warning flow FT551 not available in epics. Maybe we should create such a bit in EPICS DB. Why in this sequenc a SP FIC551 is used for the limit?
Step # | Name | Message # | Note
0 | Not running
1
2 | Filling ready |  | In Intermittent mode: wait for LI660 < LI660 Min or LI670 < LI670 Min then goto 6 or switching to PID mode and goto 4
3
4 | Regulation mode |  | Waits switching to Intermittent mode then goto 5
5 | Intermittent mode |  | Waits for LI660 < LI660 Min or LI670 < LI670 Min then goto 6 or switch to Reg mode and goto 4
6 | Start filling |  | Wait for LI660 > LI660 Max or LI670 > LI670 Max then goto 8 or switch to PID mode and goto 4
7
8 | End of filling |  | in intermittent mode wait for LI660 < LI660 Min or LI670 < LI670 Min then goto 6 or switching to PID mode and goto 4
9
10 | Stopping the SQ13A |  | This state is entered when Seq13A is stopping and it is not in state 0 nor 10 nor 12. Wait for CV603 to close then goto 12
11
12 | Stopping the SQ13A (circuit closed) |  | Wait for FV642 or FV643 to close then stop
Add string for state 5 "Intermittent mode"
Note on B4: Author: In step 6 if FT551 > SP FT551 In the PLC program it's SQ13_P_SP_CV603_FT
Note on B20: Author: Fixed 2013-03-13

## SQ14
Sequence 14: Cavity standby @ low temperature
Warning flow SQ14_FT581 not available in epics. Maybe we should create such a bit in EPICS DB. Why in this sequenc a SP FT581 is used for the limit?
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Conditioning |  | Wait for TT665 > TT665 Max or TT664 > TT665 Max then goto 6
5
6 | Cool down |  | Wait until (TT665 < TT665 Min and TT664 < TT665 Min) OR LI660/LI670 > LI660 Max/LI670 Max then goto 8
7
8 | Stop cooling |  | Wait for (TT665 > TT665 Max or TT664 > TT665 Max) AND LHe < Li6x0 Min then goto 6
9
10 | Stop Standby op. |  | Wait for FV641/FV640 to close then goto 0

## SQ15
Sequence 15: Magnet cooling down
Warning flow SQ15_PT660 not available in epics. Maybe we should create such a bit in EPICS DB. PT660 Max is used for the limit. There are more warnings in this sequence: FIC583_conditions (dT/dL and dT/dt above max limits), LIC682_conditions (FT583 and PT681 below limits), LIC683_conditions (FT581 < SP FT581 and PT660 < SP PT660)
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Wait for Yes | 1 | Have you chosen the recovery circuit for the cryostat? Waiting for Yes then goto 6
5
6 | Cooling HX680 & HX683 |  | Wait until TT680 < SP_TT680 or LT683 > SP_LT683 then goto 8
7
8 | Stop cooling |  | Wait for TT685 > P_TT685 then goto 6 OR wait for LI680 > P_LI680 Max then goto 10
9
10 | Finished cooling |  | Wait for CV601 to close then goto 12
11
12 | Regulation |  | Wait until STOP then goto 14
13
14 | Stop cooling |  | Wait until FV642 and FV680 close the goto 0
Note on B3: Author: In step 6 if PT660 > PT660 Max In the PLC program it's P_PT660_max

## SQ16
Sequence 16: Magnet, 4K operation
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Regulation |  | Waiting for State_Stopping then goto 6
5
6 | Stop 4K operation |  | Wait for CV602 and CV680 to close then goto 0

## SQ18
Sequence 18: Magnet 2K operation - control of the level and the pressure
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Regulation two baths |  | Waits for #PLC.Cryostat_2K (conditions for different sequences that are running) then goto 6
5
6 | Regulation lower bath filling |  | If quench detected - goto8 or if stopping seq 18 or 18 then goto 12
7
8 | End of filling |  | Wait until Normal_State.Ls_c and if LI680 > P_LI680_max goto 10 else if LI680 < P_LI680_max goto 14
9
10 | Cooling the magnet |  | Wait until LT682 > P_LT682 then goto 6
11
12 | Stopping cooling |  | Wait for CV602 to close then goto 0
13
14 | Regulation - two baths |  | Wait until LT682 > P_LT682_min then goto 6

## SQ17
Updated 2021-02-22
Sequence 17: Magnet, 2K operation
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Waiting for Yes/No answer | 1 | You are starting the 2K pumps, do you want to continue? If No - stop the sequence If Yes: wait for FV551 to close and depending on some other conditions goto 6 or 8
5
6 | Waiting for Yes/No answer | 2 | The 2K tank is not filled, do you want to continue? If No - stop the sequence, if Yes - go to step 8
7
8 | Cryostat connected to the recovery |  | Waiting for CV581 >= CV581 parameter then goto 10
9
10 | Prepare 2 K pump |  | Wait for FV554 to close and FV555 to open then goto 12
11
12 | Starting pumps, Waiting for Yes | 4 | Waiting for Yes, then goto 14 (when 2K pumps automatic start-up is active the sequencer program will send Yes cmd in step 5)
13
14 | Isolating 2K tank |  | Waiting for CV581 to be closed then goto 16
15
16 | 2K circuit closed |  | Waiting for FV581 and FV584 to be closed then goto 18
17
18 | Pumping 2 K tank |  | Wait until PT660 is within tollerances in "COMM_PARAM".SQ17.Low_Tol_PT660 and "COMM_PARAM".SQ17.High_Tol_PT660 then goto 20
19
20 | 2K tank pressure regulated |  | Wait for stopping and goto 22 or wait for decreasing SP PIC660 and goto 18 This can be dangerous - check if it's done accordinfg to the table or by the PID regulator. Look at Networks 15-16.
21
22 | Stop pumping |  | Wait for SQ13 stopping and FV582 to be closed then goto 24 (at exit change the state of the SQ17 mini sequence to 2)
23
24 | Pressure control | 3 | Wait for SQ13 stopping andDB_SQ13.pump2K_stopped (MUST be changed in FC117) then goto 26 Mesasge 3 is defined for this step but is not used in the transition.
25
26 | Cryostat connected to the recovery |  | Wait for PT584 go above sequence parameter PT584 then goto 28
27
28 | Stop filling line |  | Wait for FV556 to close, change state of the SQ17 mini sequence to 2 and until CV581 >= P_CV581 and set mini sequence step to 0 then goto 0

## SQ19
Sequence 19: Magnet operation - current leads cooling
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Open the cooling circuit |  | Wait for at least one current lead is selected then goto 6. If stopped goto 8
5
6 | Cooling |  | Wait until stopping state then goto 8
7
8 | End of cooling |  | Wait in State_Stopping until the flows (FT650/651/652/653) corresponding to selected current lead are set to 0 then goto 10
9
10 | Cooling the magnet |  | Wait until FV587 closes then goto 0

## SQ20
Sequence 20: Emptying the cryostat (Rev. 2019-03-13)
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment
3
4 | Prepare to L021 connection |  | Wait for FV602 to close then goto 6
5
6 | Wait for Yes/No | 1 | Is the cryogenic line L021 connected to the cryostat? Yes - goto 10; No - goto 8
7
8 | Wait for Yes/No | 2 | Do you want to stop the emptying? Yes - goto 0; No - goto 6
9
10 | Isolate Valve Box tank |  | Wait for CV601 to close then goto 12
11
12 | Cool down L021 |  | Wait for (TT645 or TT590) < SP TT645 then goto 14
13
14 | Start the transfer |  | Wait for LT590 > SP LTP590 or LI670/LI680 < SP LI670/SP LI680 then goto 16
15
16 | Stop the transfer |  | Wait for LI670/LI680 < SP LI670/SP LI680 then goto 18 OR LT590 > SP LT590 then goto 20
17
18 | Wait for Yes/No | 3 | Change level? Yes - goto 22; No - goto 26
19
20 | Wait for Yes/No | 4 | DEWAR FULL: Change level? Yes - goto 24; No - goto 26
21
22 | Wait for Yes | 5 | CRYOSTAT EMPTY: Have you defined a new level setpoint. Yes - goto 14
23
24 | Wait for Yes | 6 | DEWAR FULL: Have you defined a new level setpoint. Yes - goto 14
25
26 | Filling stopped |  | Wait for FV641 to close then goto 0
This sequence will not work unless we have a dewar with valve (CV590), level probe (LT590), pressure gauge and TT645

## SQ21
Sequence 21: Valve box warm-up (Rev. 2019-02-26)
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment |  | Equipment ok or validated then goto 10 Probably should be goto 4
3
4 | Wait for Yes/No | 1 | Do you want to start the warm-up? Yes - goto 6; No - goto 0 Jumped over
5
6 | Waiting for stopping other sequences | 2 | Waiting for "DB_SQ21".SQs_stopped (SQ9 to SQ21) then goto 8 Jumped over
7
8 | Waiting for SQ5 to stop | 3 | Waiting for SQ5 to be stopped then goto 10 Jumped over
9
10 | Wait for starting EH703 |  | Wait for starting the EH703 then goto 12
11
12 | Checking Lhe level |  | Wait for LT600 <= LT600 min then goto 14
13
14 | Waiting for starting EH600 |  | Wait for EH600 to start then goto 16
15
16 | Stopping |  | Wait for .State_Stopping then goto 0
Clean-up the PLC code - unused states and messages

## SQ22
Sequence 22: Cryostat warm-up
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment |  | Equipment ok or validated then goto 10 Probably should be goto 4
3
4 | Wait for Yes/No | 1 | Do you want to start the warm-up? Yes - goto 6; No - goto 0
5
6 | Waiting for stopping other sequences | 2 | Waiting for "DB_SQ22".SQs_stopped (SQ10 to SQ20) then goto 8
7
8 | Waiting for SQ6 to stop | 3 | Waiting for SQ6 to be stopped then goto 10
9
10 | Wait for starting EH473 |  | Wait for starting the EH473 then goto 12. For vacuum insert if seq is stopping goto 16
11
12 | Checking Lhe level |  | Wait for LI670/LI680 <= LI670 min/LI680 min then goto 14
13
14 | Heating-up |  | Wait for stop then goto 16
15
16 | Stopping |  | Wait for .State_Stopping then goto 0

## SQ23
Sequence 23: Inserts warm-up
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment |  | Equipment ok or validated then goto 10 for vacuum; goto 12 for liquid or magnet.Probably should be goto 4
3
4 | Wait for Yes/No | 1 | Do you want to start the warm-up? Yes - goto 6; No - goto 0
5
6 | Waiting for stopping other sequences | 2 | Waiting for "DB_SQ23".SQs_stopped (SQ10 to SQ20) then goto 8 for vacuum insert or goto 12 for other inserts
7
8 | Waiting for SQ7 to stop | 3 | Waiting for SQ7 to be stopped then goto 10
9
10 | Wait for starting EH765 |  | Wait for starting the EH765 then goto 12.
11
12 | Checking Lhe level |  | Wait for LI660/LI670/LI680 <= LI660 min/LI670 min/LI680 min then goto 14
13
14 | Warming-up. Waiting for stop |  | Wait for .State_Stopping then goto 0

## SQ24
Sequence 24: Cryostat isolated or connected to He recovery
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment |  | Equipment ok or validated then goto 2
3
4 | Not isolated |  | Wait for checkbox Isolated then goto 6
5
6 | Isolated |  | Waiting for PT660 > Max Pressure OR PT681 > Max Pressure (for magnet) then goto 8. Possible to uncheck the Isolated (goes to 4) or stop the seq.
7
8 | Pressure alarm |  | Waiting for ACK_GENE (goes to 6) or Stop

## SQ25
Sequence 25: Valve box isolated or connected to He recovery
Step # | Name | Message # | Note
0 | Not running
1 | Check parameters
2 | Check equipment |  | Equipment ok or validated then goto 2
3
4 | Not isolated |  | Wait for checkbox Isolated then goto 6
5
6 | Isolated |  | Waiting for PT600 > Max Pressure then goto 8. Possible to uncheck the Isolated (goes to 4) or stop the seq.
7
8 | Pressure alarm |  | Waiting for ACK_GENE (goes to 6) or Stop